## Input data
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Condenser sizing calculation tool
| Input | [9 empty] | Results
[6 empty] | Orientation |  |  |  |  | Heat exchange area | 13.1339 | m2
[5 empty] | Condenser | Horizontal |  |  |  |  | Number of tubes | 90
[11 empty] | Tube length | 2.4384 | m
|  | Tout |  |  |  |  | Tin | Cooling fluid |  |  | Number of passes | 2
|  | 40 |  |  |  |  | 10 | Water |  |  | Overall heat exchange coefficient | 1529.3694
| Vapor | Tin |  |  |  |  | Tout
| Steam | 100 |  |  |  |  | 100 | Condensation at saturation temperature
| Vapor | [5 empty] | Cooling fluid
| Name |  | Steam |  |  |  | Name |  | Water
| Temperature of condensation | Thcond | 100 | c |  |  | Temperature inlet | Tc_in | 10 | c
| Flowrate |  | 0.5 | kg/s |  |  | Temperature outlet | Tc_out | 40 | c
| Latent heat |  | 2256.4 | kJ/kg |  |  | Specific heat capacity | Cp` | 4.18 | kJ/kg/c
| Specific heat capacity of condensate |  | 4.18 | kJ/kg |  |  | Flowrate |  | 9 | kg/s
To be efficient, the calculation tool requires to express the physical properties as a function of the temperature
If you spot a mistake or wish to suggest an improvement, please contact powder.process@protonmail.com
Copyright www.PowderProcess.net
The content of PowderProcess.net is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN

## Surface requirements
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
| Heat flux hot side | 1128.2 | kW
| Heat flux cold side | 1128.6 | kW
| Difference in between values | -0.03544% | Ok
If the values are NOT equal, please review the fluid input data
| Estimated overall heat transfer coefficient | H | 1.3 | kW/m2.K
| Tvapor in |  | 100
| Tcooling in |  | 10
| Tcondensate out |  | 100
| Tcooling out |  | 40
| DT1 |  | 90
| DT2 |  | 60
| Dtml |  | 73.9891
| Required HX area | S | 11.7335 | m2

## Condenser geometry & surf calc
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Please select a condenser geometry allowing a larger surface than the calculated one
Please use standard shell tube HX geometry
| Pass tubes | 2
| Rear end type | S
| Shell inside diameter | 387 | mm
| Tube outside diameter | 0.75 | inch
|  | 0.01905 | m
| Tube inside diameter | 0.01485 | m
| Tube pitch | Square
| Pitch length | 1 | inch
|  | 0.0254 | m
| Tube count | 90
| Tube length | 8 | ft
|  | 2.4384 | m
| Material of tubes | Mild steel
| Conductivity of tubes | 66
| Heat exchange area | 13.1339 | m2
| Required | 11.7335 | m2
| HX area calculated > HX area required ? | Ok

## Tfilm initialization
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Initialization
| Thcond | 100 | c
| Tf | 25 | c
| do | 0.01905 | m
| di | 0.01485 | m
| Twall | 67.146 | c
| Tfilm | 83.573 | c

## htube
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Cooling fluid
| Tin | 10
| Tout | 40
| Tf | 25
| Twall | 62.5 | c | Use Twall from Tfilm initialization for 1st calculation, then use value from Tfilm iteration afterwards
| Flowrate | 9 | kg/s
| Density | 998.8138 | kg/m3 | use correlation as a function of T if possible
| Viscosity | 0.00089211 | Pa.s | use correlation as a function of T if possible
| Viscosity at tube T | 0.0004509 | Pa.s | use correlation as a function of T if possible
| Specific heat capacity | 4.18 | kJ/kg/c | use correlation as a function of T if possible
| Thermal conductivity | 0.6063 | W/mK | use correlation as a function of T if possible
| Heat exchanger characteristics |  | m
| di | 0.01485
| Tube length | 2.4384 | m
| Tube cross section | 0.0001732 | m2
| Number of tubes | 90
| Pass tube | 2
| Total passing area | 0.015588 | m2
| Fluid velocity | 1.1561 | m/s
| Reynolds | 19221.813
| Prandlt | 6.1505
Laminar flow
| Nusselt | 18.3418
| htube | 748.8629 | (W.m-2.K-1)
Turbulent flow
| Nusselt | 145.4975
| htube | 5940.4129 | (W.m-2.K-1)
| htube | 5940.4129

## hshell
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
| Condenser orientation | Horizontal
| hshell | 4619.2095
| Tfilm | 81.3 | Use Tfilm from Tfilm initialization for 1st calculation, then use value from Tfilm iteration afterwards
| Horizontal tubes |  |  | Vertical Tubes
| Vapor |  |  | Vapor
| Thcond | 100 |  | Thcond | 100
| Tfilm | 81.3 | c | Tfilm | 81.3 | c
| Flowrate | 0.5 | kg/s | Flowrate | 0.5 | kg/s
| Density of condensate | 960.9188 | kg/m3 | Density of condensate | 960.9188 | kg/m3
| Viscosity of condensate | 0.00028319 | Pa.s | Viscosity of condensate | 0.001 | Pa.s
| Viscosity of condensate at tube T | 0.00035001 | Pa.s | Viscosity of condensate at tube T | 0.0009 | Pa.s
| Specific heat capacity | 4.18 | kJ/kg/c | Specific heat capacity | 4.18 | kJ/kg/c
| Thermal conductivity of condensate | 0.62 | W/mK | Thermal conductivity of condensate | 0.62 | W/mK
| Heat exchanger characteristics |  |  | Heat exchanger characteristics
| do | 0.01905 |  | do | 0.01905
| Tube length | 2.4384 | m | Tube length | 2.4384 | m
| Number of tubes | 90 |  | Number of tubes | 90
| mass flowrate of condensate per unit of length of tube | 0.066574 |  | mass flowrate of condensate per unit of length of tube | 0.092829
| Reynolds | 940.337 |  | Reynolds | 371.3151
| hshell | 4619.2095 |  | hshell (Laminar flow) | 2643.2746
|  |  |  | hshell (Laminar flow) | 1047.4094
|  |  |  | hshell | 2643.2746

## Tfilm iteration
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Initialization
| Thcond | 100 | c
| Tf | 25 | c
| do | 0.01905 | m
| di | 0.01485 | m
| htube | 5910 |  | Copy here the value of htube calculated
| hshell | 4622 |  | Copy here the value of hshell calculated
| Twall | 62.5609 | c
| Tfilm | 81.2805 | c

## H calculated
DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
| htube | 5940.4129
| Rtube | 9e-05
| hshell | 2643.2746
| Rsheel | 7e-05
| Tube internal diameter | 0.015875
| Tube outside diameter | 0.01905
| Thermal conductivity | 66
| Overall heat transfer coefficient | Hcalculated | 1529.3694
|  | Hrequired | 1300
|  | Hcalculated > Hrequired | Ok
|  | Hcalculated >> Hrequired ? | No, the design is Ok